ENGR 2103

Integration of Nuclear Systems and Components

Final Exam – Summer 2024

This is a multiple-choice final examination. You may use any resources that you want to complete the exam. However, all work should be your own. The exam is due by 6:00 pm on Monday, August 12, 2024.

If you desire, you may explain your answers. If you do this, I will give partial credit where appropriate. Each question is worth 4 points.

Please email your completed exam to Dave Helling at both of these addresses: davidh179@gmail.com and hellindw@westinghouse.com.

100 Total Points

Name: ______ _____________________________

Grade: ___________________________________

- In a Pressurized Water Reactor (PWR) core axial flux (ΔI) is too negative. (Two much power being produced in the bottom of the core.)  As the Reactor Operator, what action would you take to correct this issue?

- Dilute to allow rod insertion

- Borate to allow rod insertion

- Borate to allow rod withdrawal

- Dilute to allow rod withdrawal

2.  A Boiling Water Reactor (BWR) nuclear power plant has been operating at full power for several months. Following a normal reactor shutdown, steam production will continue for a period of time, with the rate (Btu/hr) of steam production dependent upon the...

A. rate of reactor power decrease from full power to the point of adding heat.

B. pressure being maintained in the reactor pressure vessel (RPV).

C. previous power history of the plant and the time elapsed since shutdown.

D. recirculation flow rate and the water level being maintained in the RPV.

3. List at least two factors that made the Fukushima accident different from the TMI or Chernobyl accidents.

4. The reactor is shut down on natural circulation.  Decay heat generation is equivalent to 2.0% rated thermal power.  Core ΔT is stable at 30ºF.   When decay heat generation reduces to 0.5% rated thermal power, what is core ΔT?

Remember:  and

- 3.75 ºF

- 11.9 ºF

- 1.9 ºF

- 7.5 ºF

5. A cooling water pump is being driven by an ac induction motor. Which one of the following describes how and why pump motor current will change if the pump shaft shears?

A. Decreases due to decreased pump work

B. Decreases due to decreased counter electromotive force

C. Increases due to increased pump work

D. Increases due to increased counter electromotive force

6.   A nuclear power plant is operating at steady-state 100% power. Assuming that condenser cooling water inlet temperature and flow rate do not change, if condenser vacuum decreases, condensate temperature will

A. increase because condensate subcooling has decreased.

B. increase because condenser saturation pressure has increased.

C. decrease because condensate subcooling has increased.

D. decrease because condenser saturation pressure has decreased.

7.  A Boiling Water Reactor (BWR) nuclear power plant is operating at 70% of rated power when one recirculation pump trips. Reactor power will initially __________ because of the effects of the __________ coefficient.

A. decrease; void

B. increase; moderator temperature

C. decrease; moderator temperature

D. increase; void

8.   If the discharge valve of a large motor-driven centrifugal pump is kept closed during a normal pump start, the amps indication for the ac induction motor will rise to...

A. several times the full-load current value and then decrease to the no-load current value.

B. approximately the full-load current value and then decrease to the no-load current value.

C. several times the full-load current value and then decrease to the full-load value.

D. approximately the full-load current value and then stabilize at the full-load current value.

9.   In pressurized water reactors an industry issue exists, INDUSTRY ISSUE: POTENTIAL LOSS OF HIGH PRESSURE INJECTION/CHARGING CAPABILITY FROM GAS INTRUSION.  This industry issue could contribute to:

  - The probability of fuel damage increases significantly if the High Pressure Injection pumps are unavailable during a small-break loss-of-coolant accident (LOCA). With the HPI system unavailable, and if break flow is insufficient to depressurize the reactor coolant system to allow low pressure injection systems to restore core cooling and replenish reactor vessel inventory, operator actions might not be successful in preventing core damage.

  - Loss of ability to inject boric acid.  Possible re-criticality during main steam line break or other uncontrolled cool down.

  - Losses of RCP seal injection.  Could contribute to multiple seal failures and a loss of coolant accident if component cooling becomes unavailable.

    - 1.

    - 2

    - 3

    - All of the above

10. Refer to the drawing of an operating water cleanup system. All valves are identical and are initially 50% open (see figure below).

To raise the temperature at point 7, the operator should adjust valve __________ in the close direction.

A. A

B. B

C. C

D. D

11.  A main steam line break worst case is ____________ because the moderator temperature coefficient is at its most ______________ value.

- Beginning of life, positive

- Beginning of life, negative

- End of life, Positive

- End of life, negative

12.  The discharge valve for a large operating centrifugal pump should be positioned slowly to minimize the...

A. change in available net positive suction head.

B. potential for causing water hammer.

C. differential pressure stress exerted on the valve disk and stem.

D. mechanical wear on the valve seat and stem packing.

13.  In a pressurized water reactor (PWR) an inadvertent boration takes place lowering Tavg.  Reactor Power remains the same, Shutdown Margin (SDM) _____________.

- Increases

- Decreases

- Remains the same

- Initially increases then returns to pre-event value at a lower Tavg

14.  A main generator that is connected to an infinite power grid has the following initial indications:

100 MW

0 MVAR

2,900 amps

20,000 VAC

If main generator excitation is reduced slightly, amps will __________ and MW will ___________.

A. increase; decrease

B. decrease; decrease

C. increase; remain the same

D. decrease; remain the same

15.  In a PWR, a unit down power to 25% is performed on midnight shift for feedwater regulation valve work.  When power reaches 25% the power reduction stops and the operator matches Tavg to Tref.  1 Hour later the reactor operator will need to _____________________ to maintain Tavg due to  __________________.

- Dilute, Xenon decay

- Dilute, Xenon buildup

- Borate, Xenon decay

- Borate, Xenon decay

16.  A Boiling Water Reactor (BWR) nuclear power plant is operating at 70% of rated power when one recirculation pump trips. Reactor power will initially __________ because of the effects of the __________ coefficient.

A. decrease; void

B. increase; moderator temperature

C. decrease; moderator temperature

D. increase; void

17.  The power factor is adjusted on a Main Unit Generator.  The adjustment will cause __________ and  __________  to change while maintaining _______________ the same.

A.  Real Power and Reactive Power

Apparent Power

- MVA and MW

MVAR

- Apparent Power and Reactive Power

Real Power

- MW and MVAR

MVA

18.   Real Power is 970 MW and Reactive Power is 230 MVAR.  What is the power factor?

- 0.973

- 0.901

- 0.912

- 0.954

19.  Initial conditions 100% power.  A control rod drops into the reactor with no reactor trip.  Long term:

Tavg __________________

Reactor power __________________

Shutdown margin _________________

Steam pressure _________________

      - Decreases, decreases, increases, increases

      - Increases, decreases, decreases, decreases

C.  Decreases, remains the same, remains the same, decreases

D.  Increases, remains the same, remains the same, decreases

20.  At a pressurized water reactor (PWR) a steam generator tube rupture takes place.  The emergency operating procedures will identify and isolate the ruptured steam generator.  A cooldown of the reactor coolant system (RCS) will __________.

- Lower the steam generator pressure to reduce reactor coolant leakage

- Lower the reactor coolant temperature to allow RCS to be de-pressurized

- Decrease subcooling

- Ensure a steam generator safety valve lift setpoint is not challenged

21.  In a Westinghouse pressurized water reactor (PWR) a loss of all AC (emergency and normal) occurs.  The ___________ driven auxiliary feedwater pump will be used to supply auxiliary feedwater to the steam generator.  The RCS will be cooled to allow the injection of borated water from the _____________   Cool down of the RCS will be stopped due to  ___________  concerns

- Motor, accumulators, Nitrogen

- Steam , Refueling water storage tank, brittle fracture

- Steam, accumulators, nitrogen

- Steam, volume control tank (VCT), brittle fracture

22.  The overall objective and logic of 10CFR50.48 Appendix R is to:

- Maximize the use of air operated valves (AOV’s) due to the fail safe position of the valves

- Minimize the use of electrical powered equipment necessary for hot shutdown and subsequent cooldown

- Initiate safety injection to ensure adequate reactor vessel level is maintained for hot shutdown from outside the control room and subsequent cooldown of the reactor plant

- Maximize the use of electrical powered equipment to ensure fire fighting activities can be accomplished

23.   A Boiling Water Reactor (BWR) nuclear power plant is operating at 90% of rated power near the end of a fuel cycle. If a turbine control system malfunction opens the turbine control valves an additional 5 percent, reactor power will initially.

A. increase due to positive reactivity addition from the void coefficient only.

B. increase due to positive reactivity addition from the void and moderator temperature coefficients.

C. decrease due to negative reactivity addition from the void coefficient only.

D. decrease due to negative reactivity addition from the void and moderator temperature coefficients.

24.  On a running pump at shutoff head there is _______________ and ___________________ current draw, at runout there is ____________ and __________________ current draw.

- Low flow, low amp,  high flow, high amp

- High flow, low amp,  low flow high amp

- Low flow, high amp, high flow high amp

- High flow, high amp, low flow, low amp

25.  A technical specification level transmitter has failed on the reactor coolant pressurizer (requires 2 out of 3 channels tripped to produce an ESF actuation).  Instrument & Control (I&C) has tripped the failed transmitter bistables.  For the ESF actuation to take place ____________________.

- 2 operable channels must trip inputting into 1 out of 2 logic bays

- 1 operable channel must trip inputting into 2 out of 2 logic bays

- 1 operable channel must trip inputting into 1 out of 2 logic bays

- 2 operable channels must trip inputting into 2 out of 2 logic bays